# POLICY GUIDELINES

A formal process has been developed for the completion of an annual Fire Door Assembly Inspection (FDAI) within the facility in compliance with current Life Safety Code regulations as enforced by the Centers for Medicare and Medicaid Services (CMS), its contractors, and other Authorities Having Jurisdiction (AHJ).

# DEFINITIONS

A Fire Door Assembly (FDA) is a door, hardware, and associated frame that is part of a passive fire protection system installed in either a fire-rated wall/barrier or non-fire rated wall/barrier to provide protection of an opening to help reduce the spread of smoke and/or fire between smoke compartments and other areas of a building, including individual rooms. To qualify as a FDA, the door, frame, and associated hardware must be listed with a testing laboratory for use on a fire-rated door assembly. In most cases, a label or stamp will be installed on the door and frame indicating that they are rated.

A Fire Door Assembly Inspection (FDAI) is a comprehensive process performed within all CMS-licensed healthcare facilities that includes a thorough and documented evaluation of every Fire Door Assembly (FDA) in accordance with the 2010 edition of NFPA 80 (Standard for Fire Doors and Other Protection Openings) as required by the 2012 edition of NFPA 101 (The Life Safety Code).

A Fire Door Assembly Inspection (FDAI) Checklist is a document used for guidance as well as to illustrate the findings of the annual inspection of every Fire Door Assembly (FDA) within a licensed healthcare facility in accordance with the 2010 edition of NFPA 80 (Standard for Fire Doors and Other Protection Openings) as required by the 2012 edition of NFPA 101 (The Life Safety Code).

A Fire Door Assembly Inspection (FDAI) Master Inventory List is a document used to itemize and illustrate the completion of the annual inspection process on all FDAs within a facility in accordance with the 2010 edition of NFPA 80 (Standard for Fire Doors and Other Protection Openings) as required by the 2012 edition of NFPA 101 (The Life Safety Code).

# PROCEDURAL COMPONENTS

## Inspection Process

### A Fire Door Assembly Inspection (FDAI) shall be conducted on all Fire Door Assemblies (FDA) within the facility, whether they are installed in a fire-rated wall or barrier, or not. If a FDA is present within the facility, it requires an annual FDAI in accordance with regulations

### The FDAI Checklist shall be used at all facilities as a guideline to conduct the required annual inspection process. A single checklist shall be used for each FDAI that is conducted on an annual basis. The checklist should be used to guide qualified staff members who perform the FDAI in order to complete the process in a standardized manner, as well as to document the process, including evaluation of the following components:

#### Door

#### Frame

#### Operation

#### Hinges / Pivot

#### Flush Bolts / Coordinator

#### Lockset / Latchset

#### Fire Exit Hardware

#### Door Closer

#### Other

When utilizing the checklist, all required areas of the document should be completed, including the general information at the top of the form. Check marks should only be inserted in a specific field on the checklist when the element identified is found to be in a condition that is not compliant. If a check is inserted, a corresponding work order number should be inserted in the space provided next to the item that is identified as non-compliant. There is also space at the bottom of the checklist for notes and a space requiring the signature of the person conducting the FDAI.

### A schedule should be developed to ensure that the FDAI process is completed on an annual basis, as required. This process should be programmed into each facility’s preventative maintenance schedule.

### Upon completion of the FDAI, an entry shall be made on the Fire Door Assembly Inspection Master Inventory List itemizing the following information:

#### Door ID Number

#### Door Location

#### Date of FDAI

#### Designation of Either Pass or Fail

#### Work Order Number(s) Assigned

#### Date of Correction

#### Name of Person Conducting FDAI

## Resources

### Pendulum Fire Door Assembly Inspection (FDAI) Checklist

### Pendulum Fire Door Assembly Inspection (FDAI) Master Inventory List

### Pendulum Fire Door Assembly Inspection (FDAI) Training Webinar

## References

### NFPA 80, 2010 Edition- Standard for Fire Doors and Other Protective Openings

### NFPA 101, 2012 Edition- The Life Safety Code

### Nursing Homes - Section 1819(d) of the Social Security Act

### Nursing Homes - 42 CFR 483.70(a)

## Qualifications

### NFPA 80, 2010 Edition- Standard for Fire Doors and Other Protective Openings states the following pertaining to the qualifications of the person(s) performing the FDAI:  “Functional testing of fire doors and window assemblies shall be performed by individuals with knowledge and understanding of the operating components of the type of door being subject to testing”

### According to CMS’ interpretation of the language cited in NFPA 80, 2010 Edition regarding qualifications, those persons employed by the facility and working as maintenance workers or maintenance supervisors at a facility are qualified to conduct the FDAI process on an annual basis

## Education

### Maintenance personnel who perform the Annual FDAI within a facility should view the Pendulum training webinar that was been produced as a resource for this program

### Additional training is recommended whenever it can be obtained from other Subject Matter Experts (SME) who may be accessible through training programs sponsored by vendors, trade associations, professional organizations, and other reliable sources to enhance the knowledge-base of those performing the Annual FDAI